| Compliance Checklist (S104 Adoption) |  |  |  |
| --- | --- | --- | --- |
|  | Compliant |  |  |
| Layout | Foul | Surface | Comments |
| Sewer Location | Y / N | Y/N |  |
| Adoptable sewers are laid in Adoptable / Public Highway and/or Public-Open-Space in accordance with DCG B5.1. NB: Sewers serving <10 properties can be located within front gardens if 3m clearance is maintained from buildings. |  |  |  |
| Kerb Lines | Y / N | Y / N |  |
| Sewers and manholes are positioned a suitable distance from the kerb line in accordance with DCG B5.1.12. Sewers are 1m, and manholes are 0.5m, from outside edge to the kerb line. |  |  |  |
| Tree Positioning | Y / N | Y / N |  |
| Tree and Landscaping proposals have been submitted and comply with DCG B5.10 and B7.6 |  |  |  |
| Distance to Buildings | Y / N | Y/N |  |
| No buildings are proposed within the protection strip for any existing and/or adoptable public sewers. NB: Size of protection strip stipulated in DCG B5.1 |  |  |  |
| Other | Y / N | Y/N |  |
|  | Compliant |  |  |
| Access Points | Foul | Surface | Comments |
| Requirement | Y / N | Y / N |  |
| Access points are required at all changes in direction, pipe diameter, gradient and where 2 or more sewers connect. Distance between access points should comply with DCG B5.2 |  |  |  |
| Types | Y / N | Y / N |  |
| Appropriate access points have been used and detailed. NB: Refer to DCG B5.2 and Figure B 3. Where manhole depth >6m a ‘special’ manhole detail will be required. |  |  |  |
| Diameters | Y / N | Y / N |  |
| Manhole diameters (Type A, B and C only) are in accordance with DCG B5.2.12 and Table B 1. Manhole diameters take into account minimum benching requirements as per B5.2.12.1 & B5.2.29 |  |  |  |
| Covers & Frames | Y / N | Y / N |  |
| Covers and frames for manhole chambers and inspection chambers are in accordance with DCG B5.2.18 – B5.2.22 |  |  |  |
| Rocker Pipes | Y / N | Y / N |  |
| Rocker pipes are provided in accordance with DCG B5.2.24 requirements. Their length is in accordance with DCG Table E 13 (see E6.6). |  |  |  |
| Backdrops | Y / N | Y / N |  |
| Steeper gradients are preferred to the use of backdrops (see DCG B5.2.27). If required then they should be constructed at manholes as shown in DCG Figure B 16 and Figure B 17. Ramped backdrops should be used rather than vertical backdrops |  |  |  |
| Access / Fittings | Y / N | Y / N |  |
| Minimum access opening sizes and fitting requirements are in accordance with DCG B5.2 |  |  |  |
| Other | Y / N | Y / N |  |

|  | Compliant |  |  |
| --- | --- | --- | --- |
| Sewers | Foul | Surface | Comments |
| Depths | Y / N | Y / N |  |
| Adoptable sewers and lateral drains have minimum cover in accordance with DCG B5.1 and if not, measures have been taken to protect them in accordance with DCG B7. |  |  |  |
| Surface Water Drainage Components – General All surface water drainage components proposed for adoption comply with the requirements outlined in DCG Part C1 to C5. |  | Y / N |  |
| Surface Water Drainage Components - Design |  | Y / N |  |
| All surface water drainage components are in accordance with DCG Part C6 and C7 requirements (where appropriate). |  |  |  |
| Hydraulic Design – Foul | Y / N |  |  |
| Do sewers achieve a velocity of 0.75m/s at 1/3 design flow? If not, do the gradients satisfy criteria in DCG B6? i.e. 100mm dia’ 2-9 properties connected at 1/80 or 150mm dia’ >10 properties connected at 1/150. (150mm dia’ 2-9 properties connected at 1/60 also acceptable). See DCG B3 and B6. |  |  |  |
| Hydraulic Design – Surface Do the surface water drainage components proposed for adoption comply with DCG Part C6 requirements? |  | Y / N |  |
| Surcharging | Y / N | Y / N |  |
| Foul sewers and lateral drains should be designed to run at no more than 75% of pipe full conditions Surface water drainage pipes should be designed under pipe full conditions (without surcharging above pipe soffit) in accordance with DCG C6.4.3 |  |  |  |
| Bedding | Y / N | Y / N |  |
| The appropriate pipe bedding details have been provided which in most cases would be a Class 'S' bed and surround. See DCG E2.25 and E5.2 |  |  |  |
| Other | Y / N | Y / N |  |

|  | Compliant |  |  |
| --- | --- | --- | --- |
| General | Foul | Surface | Comments |
| Colouring | Y / N | Y / N |  |
| Drawings are coloured as per Appendix VII of DCG with highway drains and private laterals uncoloured. |  |  |  |
| Inconsistencies | Y / N | Y / N |  |
| Pipe lengths, gradients and sizes are consistent on layout plans, long sections and design calculations. |  |  |  |
| Long Sections | Y / N | Y / N |  |
| Long section drawings also include bedding details, concrete protection (where applicable), manhole types and manhole diameters. |  |  |  |
| Outfalls/Headwalls |  | Y / N |  |
| A detail of the outfall/headwall has been provided and is in accordance with C7.11 of DCG, which includes water levels. (See Figures C1 – C 3) |  |  |  |
| Flow control device |  | Y / N |  |
| The relevant head/flow characteristics curve and installation details been provided. All flow control devices are designed in accordance with C7.12 of DCG |  |  |  |
| Impermeable Area Plan |  | Y / N |  |
| A coloured impermeable area plan has been provided identifying areas discharging to each pipe line. |  |  |  |
| Private Connections | Y / N | Y / N |  |
| Private connections to the adoptable sewers are a minimum 100mm diameter and laid soffit to soffit. |  |  |  |
| Connections to the Public Sewer | Y / N | Y / N |  |
| The existing levels of the public sewer and positions of other utility apparatus have been established. |  |  |  |
| Other | Y / N | Y / N |  |